City of Scottsdale

This application must be completed in full in order to proceed with new main water quality testing in the City of Scottsdale. A final copy of the approval letter will be attached to the online permit.

New Main Disinfection Plan

Please check all items:

- Project Name: _______________________________________________________________

Project Address/Crossroads: _____________________________________________________

City Permit #: ________________________________________________________________

City Inspector: _______________________________________________________________

- Onsite Contact

Name                                                 Company                          Phone                     Email

_________________________    ________________      ___________      _______________

_________________________    ________________      ___________      _______________

- Potable Water

Source Water: ___________________________ Approved Meter/Backflow:     Y  /  N  /  NA___

- Disinfection

Method per MAG611 / AWWA C651:  _________________________________________________

Scheduled Disinfection Date and Time: __________________Sample Date: ___________________

- Water Flushing

Discharge Location:  _________________________________________________

Dechlorination Method: _______________________________________________

Calculated Volume/Rate/Duration:  _________________________________________________

- Plan Sheet(s) Attach to this Form

New Main Length (ft): ___________________________  Mains Shown on Plan: ___Y  /  N ______

Feed Point Identified: ____Y  /  N______ Water Meter/Backflow Device Shown: ___Y  /  N_______ Number of Sampling Locations: ___________ Sampling Riser/ Hose Bibs Shown: ___Y  /  N_______

Valve and Hydrant Locations Identified: ___Y  /  N  _____

- Contractor Acknowledgements

Pressure testing and debris flushing will be completed prior to disinfection. ____  Y  /  N_____

All work to follow consecutive day sampling schedule.                             Y  /  N______

Main will remain isolated until bacteriological results pass.                           Y  /  N_____

Requirements for New Main Testing for City of Scottsdale

- Overview: The Water Quality Department is tasked with verifying that newly installed sections of water mains have been adequately disinfected prior to connection with existing water mains. Mains less than 100 ft may disinfect with a spray and swab technique and those greater than 3000ft will need to be completed in phases. The department requires that contractors follow the guidelines outlined in MAG Specs 6111 or AWWA C651. See the City of Scottsdale website https://www.scottsdaleaz.gov/water/water-service/commercial-services for more information on new main requirements. The plan may be completed by a project contractor or city inspector.

- Scheduling: A completed New Main Disinfection Plan must be emailed to the water quality group before new main sampling can begin. It is required to be emailed at least two working business days before the sampling event. Plans submitted after 4:30pm local time will be considered as sent the next day. All plans must be emailed to waterqualitygroup@scottsdaleaz.gov and it is recommended to CC the city inspector. Day 1 sampling will only occur Monday through Wednesday and is subject to holiday impacts. Field staff work Monday to Thursday.

- Sample Taps: Contractor will provide taps where samples will be collected in a safe manner. To prevent potential contamination sample taps must be located 18 inches above grade and utilize a flow control tap. Water staff may require additional taps be provided if deemed necessary to obtain adequate representative sampling.

- Verification of High Range Cl: WQ staff will verify that the free chlorine residual in the new main is higher than 10 ppm at all sample taps after 24 hours from initial chlorination and no more than 48 hours. The chlorination method used must conform to NSF/ANSI 60 & 61 and the AWWA C651 Standards. Inadequate chlorine residual at any point will require rechlorination. Disinfection by Slug Method requires prior approval.

- Flushing: After chlorination levels have been verified by WQ staff, the contractor is clear to flush the main with potable water until the cl residual drops to ambient levels or less than 2.0 ppm.

- Day 1 Microbiological Sampling: WQ staff will verify that free chlorine residual is below 2.0ppm before collecting a microbiological sample from each of the sample taps. Flushing will need to continue until it is and must be completed by 2:00pm for Day 1 sampling to occur.

- Day 2 Microbiological Sampling: WQ staff will repeat sampling completed from Day 1 sampling.

- Results: Analysis requires 48 hours. Results will be updated in the permit portal by the inspector and a system generated email notification will be provided to any permit contacts. An acceptance letter will be added to permit attachments once complete. A failed test will require the process to start over. For more information, please contact the Water Quality Department at 480-312-5668.

By signing and dating below you acknowledge and understand the requirements for New Main Disinfection Testing in the City of Scottsdale.

Failure to follow any of the requirements may result in the delay or cancelation of disinfection testing and approval. Contact will be notified at least one business day advance.

________________________________         _______________________            _____________ Contractor/Applicant                                         Signature                                             Date